## Main
Distributed Architecture Rectifier and Battery Balancer
Balances only the following: Batteries & Rectifiers, Batteries Only, or RectifiersOnly | [12 empty] | Cell Color Key
Batteries and Rectifiers are Balanced to Loads. | [12 empty] | Cells for your data entery are Green | [30 empty] | Lists for Data Validation
[13 empty] | Bus Bar Currents High due to Correctable Imbalance are shown as Red | [30 empty] | Connects per Battery | Yes / No
Float V |  | 52.8 | [10 empty] | Bus Bar Currents Reduced by Balancing are shown as Green | [30 empty] | 1 | Yes
End of Dishcarge V |  | 42 | [10 empty] | Recharge Factor not meeting target are shown as Gold | [30 empty] | 2 | No
| Battery Connections | 1 | Number of Frames to which each string (section) may be cabled | [9 empty] | Changes Made to Balance are shown as Rose | [30 empty] | 3
Rectifier Rating A |  | 220 | Maximum Recharge Current | [40 empty] | 4
Recharge Factor |  |  | Target | 1.15 | [8 empty] | Worksheet is protected to prevent accidental changes in formulae. To unprotect or re-protect: Tools ¦ Protection
Actual Recharge Factor |  |  |  | 1.3632 |  | Bus Bar Currents
Rectifiers for Target Recharge Factor |  |  |  | 60.7409 |  | positive |  | negative
[6 empty] | ð |  | ï |  |  |  |  | Only Frames with Rectifier Positions, Battery Strings, or Load are considered present. Add a frame - add one of them to the frame. Remove a frame - delete all of them.
System Totals
Original System
Frame |  | System |  |  | 1 |  | 2 |  | 3 |  | 4 |  | 5 |  | 6 |  | 7 |  | 8 |  | 9 |  | 10 |  | 11 |  | 12 |  | 13 |  | 14 |  | 15 |  | 16 |  | 17 |  | 18 |  | 19 |  | 20 |  |  | 0
Rectifier Positions |  | 80 |  |  | 4 |  | 4 |  | 4 |  | 4 |  | 4 |  | 4 |  | 4 |  | 4 |  | 4 |  | 4 |  | 4 |  | 4 |  | 4 |  | 4 |  | 4 |  | 4 |  | 4 |  | 4 |  | 4 |  | 4
Rectifiers |  | 72 |  |  | 4 |  | 4 |  | 4 |  | 4 |  | 3 |  | 3 |  | 3 |  | 3 |  | 3 |  | 3 |  | 3 |  | 3 |  | 4 |  | 4 |  | 4 |  | 4 |  | 4 |  | 4 |  | 4 |  | 4
Battery Strings |  | 20 |  |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1
| Frames Present | 20 |  |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1
Float Currents | Load | 11620 |  |  | 480 |  | 720 |  | 480 |  | 600 |  | 480 |  | 600 |  | 480 |  | 720 |  | 720 |  | 720 |  | 720 |  | 480 |  | 720 |  | 480 |  | 720 |  | 480 |  | 720 |  | 220 |  | 600 |  | 480
| Rectifier | 11620 |  |  | 645.5556 |  | 645.5556 |  | 645.5556 |  | 645.5556 |  | 484.1667 |  | 484.1667 |  | 484.1667 |  | 484.1667 |  | 484.1667 |  | 484.1667 |  | 484.1667 |  | 484.1667 |  | 645.5556 |  | 645.5556 |  | 645.5556 |  | 645.5556 |  | 645.5556 |  | 645.5556 |  | 645.5556 |  | 645.5556
| Bus Bars | 818.8889 | max |  |  | 165.5556 |  | 91.1111 |  | 256.6667 |  | 302.2222 |  | 306.3889 |  | 190.5556 |  | 194.7222 |  | -41.1111 |  | -276.9444 |  | -512.7778 |  | -748.6111 |  | -744.4444 |  | -818.8889 |  | -653.3333 |  | -727.7778 |  | -562.2222 |  | -636.6667 |  | -211.1111 |  | -165.5556
|  | 400.3509 | avg |  |  | ð |  | ð |  | ð |  | ð |  | ð |  | ð |  | ð |  | ï |  | ï |  | ï |  | ï |  | ï |  | ï |  | ï |  | ï |  | ï |  | ï |  | ï |  | ï
End of Discharge | Load | 14608 |  |  | 603.4286 |  | 905.1429 |  | 603.4286 |  | 754.2857 |  | 603.4286 |  | 754.2857 |  | 603.4286 |  | 905.1429 |  | 905.1429 |  | 905.1429 |  | 905.1429 |  | 603.4286 |  | 905.1429 |  | 603.4286 |  | 905.1429 |  | 603.4286 |  | 905.1429 |  | 276.5714 |  | 754.2857 |  | 603.4286
| Batteries | 14608 |  |  | 730.4 |  | 730.4 |  | 730.4 |  | 730.4 |  | 730.4 |  | 730.4 |  | 730.4 |  | 730.4 |  | 730.4 |  | 730.4 |  | 730.4 |  | 730.4 |  | 730.4 |  | 730.4 |  | 730.4 |  | 730.4 |  | 730.4 |  | 730.4 |  | 730.4 |  | 730.4
| Bus Bars | 556.9143 | max |  |  | 126.9714 |  | -47.7714 |  | 79.2 |  | 55.3143 |  | 182.2857 |  | 158.4 |  | 285.3714 |  | 110.6286 |  | -64.1143 |  | -238.8571 |  | -413.6 |  | -286.6286 |  | -461.3714 |  | -334.4 |  | -509.1429 |  | -382.1714 |  | -556.9143 |  | -103.0857 |  | -126.9714
|  | 238.0632 | avg |  |  | ð |  | ï |  | ð |  | ð |  | ð |  | ð |  | ð |  | ð |  | ï |  | ï |  | ï |  | ï |  | ï |  | ï |  | ï |  | ï |  | ï |  | ï |  | ï
Start of Recharge | Load | 12782 |  |  | 528 |  | 792 |  | 528 |  | 660 |  | 528 |  | 660 |  | 528 |  | 792 |  | 792 |  | 792 |  | 792 |  | 528 |  | 792 |  | 528 |  | 792 |  | 528 |  | 792 |  | 242 |  | 660 |  | 528
| Rectifiers | 15840 |  |  | 880 |  | 880 |  | 880 |  | 880 |  | 660 |  | 660 |  | 660 |  | 660 |  | 660 |  | 660 |  | 660 |  | 660 |  | 880 |  | 880 |  | 880 |  | 880 |  | 880 |  | 880 |  | 880 |  | 880
| Batteries | 3058 |  |  | 152.9 |  | 152.9 |  | 152.9 |  | 152.9 |  | 152.9 |  | 152.9 |  | 152.9 |  | 152.9 |  | 152.9 |  | 152.9 |  | 152.9 |  | 152.9 |  | 152.9 |  | 152.9 |  | 152.9 |  | 152.9 |  | 152.9 |  | 152.9 |  | 152.9 |  | 152.9
| Bus Bars | 1019.7 | max |  |  | 199.1 |  | 134.2 |  | 333.3 |  | 400.4 |  | 379.5 |  | 226.6 |  | 205.7 |  | -79.2 |  | -364.1 |  | -649 |  | -933.9 |  | -954.8 |  | -1019.7 |  | -820.6 |  | -885.5 |  | -686.4 |  | -751.3 |  | -266.2 |  | -199.1
|  | 499.4 | avg |  |  | ð |  | ð |  | ð |  | ð |  | ð |  | ð |  | ð |  | ï |  | ï |  | ï |  | ï |  | ï |  | ï |  | ï |  | ï |  | ï |  | ï |  | ï |  | ï
| Frame Averages | [6 empty] | End of Discharge Battery Currents Average | [5 empty] | Float Current Average
[5 empty] | Load (Float) Current | 581 |  |  | per String |  |  | 730.4 |  | per Rectifier |  |  | 161.3889
[5 empty] | End of Discharge Current | 730.4 |  |  | per Connection |  |  | 730.4
Batteries Connections Moved to Balanced in Discharge | [6 empty] | & | Rectifiers Moved to Balanced in Float
Frame |  | System |  |  | 1 |  | 2 |  | 3 |  | 4 |  | 5 |  | 6 |  | 7 |  | 8 |  | 9 |  | 10 |  | 11 |  | 12 |  | 13 |  | 14 |  | 15 |  | 16 |  | 17 |  | 18 |  | 19 |  | 20
Rectifiers |  | 72 |  |  | 3 |  | 4 |  | 3 |  | 4 |  | 3 |  | 4 |  | 3 |  | 4 |  | 4 |  | 4 |  | 4 |  | 4 |  | 4 |  | 4 |  | 4 |  | 3 |  | 4 |  | 2 |  | 4 |  | 3
Battery Strings |  | 20 |  |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 2 |  | 0 |  | 2 |  | 0 |  | 2 |  | 1 |  | 1 |  | 0 |  | 1 |  | 1
Float Currents | Load | 11620 |  |  | 480 |  | 720 |  | 480 |  | 600 |  | 480 |  | 600 |  | 480 |  | 720 |  | 720 |  | 720 |  | 720 |  | 480 |  | 720 |  | 480 |  | 720 |  | 480 |  | 720 |  | 220 |  | 600 |  | 480
| Rectifier | 9521.9444 |  |  | 484.1667 |  | 645.5556 |  | 484.1667 |  | 645.5556 |  | 484.1667 |  | 645.5556 |  | 484.1667 |  | 645.5556 |  | 645.5556 |  | 645.5556 |  | 645.5556 |  | 645.5556 |  | 645.5556 |  | 645.5556 |  | 645.5556 |  | 484.1667 |  | 645.5556 |  | 322.7778 |  | 645.5556 |  | 484.1667
| Bus Bars | 264.4444 | max |  |  | 4.1667 |  | -70.2778 |  | -66.1111 |  | -20.5556 |  | -16.3889 |  | 29.1667 |  | 33.3333 |  | -41.1111 |  | -115.5556 |  | -190 |  | -264.4444 |  | -98.8889 |  | -173.3333 |  | -7.7778 |  | -82.2222 |  | -78.0556 |  | -152.5 |  | -49.7222 |  | -4.1667
|  | 78.8304 | avg |  |  | ð |  | ï |  | ï |  | ï |  | ï |  | ð |  | ð |  | ï |  | ï |  | ï |  | ï |  | ï |  | ï |  | ï |  | ï |  | ï |  | ï |  | ï |  | ï
End of Discharge Currents | Load | 14608 |  |  | 603.4286 |  | 905.1429 |  | 603.4286 |  | 754.2857 |  | 603.4286 |  | 754.2857 |  | 603.4286 |  | 905.1429 |  | 905.1429 |  | 905.1429 |  | 905.1429 |  | 603.4286 |  | 905.1429 |  | 603.4286 |  | 905.1429 |  | 603.4286 |  | 905.1429 |  | 276.5714 |  | 754.2857 |  | 603.4286
| Batteries | 14608 |  |  | 730.4 |  | 730.4 |  | 730.4 |  | 730.4 |  | 730.4 |  | 730.4 |  | 730.4 |  | 730.4 |  | 730.4 |  | 730.4 |  | 1460.8 |  | 0 |  | 1460.8 |  | 0 |  | 1460.8 |  | 730.4 |  | 730.4 |  | 0 |  | 730.4 |  | 730.4
| Bus Bars | 682.6286 | max |  |  | -221.2571 |  | -396 |  | -269.0286 |  | -292.9143 |  | -165.9429 |  | -189.8286 |  | -62.8571 |  | -237.6 |  | -412.3429 |  | -587.0857 |  | -31.4286 |  | -634.8571 |  | -79.2 |  | -682.6286 |  | -126.9714 |  | 174.7429 |  | 276.5714 |  | 23.8857 |  | -126.9714
|  | 262.7429 | avg |  |  | ï |  | ï |  | ï |  | ï |  | ï |  | ï |  | ï |  | ï |  | ï |  | ï |  | ï |  | ï |  | ï |  | ï |  | ï |  | ð |  | ð |  | ð |  | ï
Start of Recharge | Load | 12782 |  |  | 528 |  | 792 |  | 528 |  | 660 |  | 528 |  | 660 |  | 528 |  | 792 |  | 792 |  | 792 |  | 792 |  | 528 |  | 792 |  | 528 |  | 792 |  | 528 |  | 792 |  | 242 |  | 660 |  | 528
| Rectifiers | 15840 |  |  | 660 |  | 880 |  | 660 |  | 880 |  | 660 |  | 880 |  | 660 |  | 880 |  | 880 |  | 880 |  | 880 |  | 880 |  | 880 |  | 880 |  | 880 |  | 660 |  | 880 |  | 440 |  | 880 |  | 660
| Batteries | 3058 |  |  | 152.9 |  | 152.9 |  | 152.9 |  | 152.9 |  | 152.9 |  | 152.9 |  | 152.9 |  | 152.9 |  | 152.9 |  | 152.9 |  | 305.8 |  | 0 |  | 305.8 |  | 0 |  | 305.8 |  | 152.9 |  | 152.9 |  | 0 |  | 152.9 |  | 152.9
| Bus Bars | 426.8 | max |  |  | -20.9 |  | -85.8 |  | -106.7 |  | -39.6 |  | -60.5 |  | 6.6 |  | -14.3 |  | -79.2 |  | -144.1 |  | -209 |  | -426.8 |  | -74.8 |  | -292.6 |  | 59.4 |  | -158.4 |  | -179.3 |  | -244.2 |  | -46.2 |  | 20.9
|  | 119.4368 | avg |  |  | ï |  | ï |  | ï |  | ï |  | ï |  | ð |  | ï |  | ï |  | ï |  | ï |  | ï |  | ï |  | ï |  | ð |  | ï |  | ï |  | ï |  | ï |  | ð
Batteries Connections Moved to Balanced in Discharge
Frame |  | System |  |  | 1 |  | 2 |  | 3 |  | 4 |  | 5 |  | 6 |  | 7 |  | 8 |  | 9 |  | 10 |  | 11 |  | 12 |  | 13 |  | 14 |  | 15 |  | 16 |  | 17 |  | 18 |  | 19 |  | 20
Battery Strings |  | 20 |  |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 2 |  | 0 |  | 2 |  | 0 |  | 2 |  | 1 |  | 1 |  | 0 |  | 1 |  | 1
| String error | 0.327 |  |  | -0.17384 |  | 0.23924 |  | -0.17384 |  | 0.032702 |  | -0.17384 |  | 0.032702 |  | -0.17384 |  | 0.23924 |  | 0.23924 |  | 0.23924 |  | -0.76076 |  | 0.82616 |  | -0.76076 |  | 0.82616 |  | -0.76076 |  | -0.17384 |  | 0.23924 |  | 0.37866 |  | 0.032702 |  | -0.17384
End of Discharge Currents | Load | 14608 |  |  | 603.4286 |  | 905.1429 |  | 603.4286 |  | 754.2857 |  | 603.4286 |  | 754.2857 |  | 603.4286 |  | 905.1429 |  | 905.1429 |  | 905.1429 |  | 905.1429 |  | 603.4286 |  | 905.1429 |  | 603.4286 |  | 905.1429 |  | 603.4286 |  | 905.1429 |  | 276.5714 |  | 754.2857 |  | 603.4286
| Batteries | 14608 |  |  | 730.4 |  | 730.4 |  | 730.4 |  | 730.4 |  | 730.4 |  | 730.4 |  | 730.4 |  | 730.4 |  | 730.4 |  | 730.4 |  | 1460.8 |  | 0 |  | 1460.8 |  | 0 |  | 1460.8 |  | 730.4 |  | 730.4 |  | 0 |  | 730.4 |  | 730.4
| Bus Bars | 682.6286 | max |  |  | -221.2571 |  | -396 |  | -269.0286 |  | -292.9143 |  | -165.9429 |  | -189.8286 |  | -62.8571 |  | -237.6 |  | -412.3429 |  | -587.0857 |  | -31.4286 |  | -634.8571 |  | -79.2 |  | -682.6286 |  | -126.9714 |  | 174.7429 |  | 276.5714 |  | 23.8857 |  | -126.9714
|  | 262.7429 | avg |  |  | ï |  | ï |  | ï |  | ï |  | ï |  | ï |  | ï |  | ï |  | ï |  | ï |  | ï |  | ï |  | ï |  | ï |  | ï |  | ð |  | ð |  | ð |  | ï
Start of Recharge | Load | 12782 |  |  | 528 |  | 792 |  | 528 |  | 660 |  | 528 |  | 660 |  | 528 |  | 792 |  | 792 |  | 792 |  | 792 |  | 528 |  | 792 |  | 528 |  | 792 |  | 528 |  | 792 |  | 242 |  | 660 |  | 528
| Rectifiers | 15840 |  |  | 880 |  | 880 |  | 880 |  | 880 |  | 660 |  | 660 |  | 660 |  | 660 |  | 660 |  | 660 |  | 660 |  | 660 |  | 880 |  | 880 |  | 880 |  | 880 |  | 880 |  | 880 |  | 880 |  | 880
| Batteries | 3058 |  |  | 152.9 |  | 152.9 |  | 152.9 |  | 152.9 |  | 152.9 |  | 152.9 |  | 152.9 |  | 152.9 |  | 152.9 |  | 152.9 |  | 305.8 |  | 0 |  | 305.8 |  | 0 |  | 305.8 |  | 152.9 |  | 152.9 |  | 0 |  | 152.9 |  | 152.9
| Bus Bars | 1172.6 | max |  |  | 199.1 |  | 134.2 |  | 333.3 |  | 400.4 |  | 379.5 |  | 226.6 |  | 205.7 |  | -79.2 |  | -364.1 |  | -649 |  | -1086.8 |  | -954.8 |  | -1172.6 |  | -820.6 |  | -1038.4 |  | -839.3 |  | -904.2 |  | -266.2 |  | -199.1
|  | 539.6368 | avg |  |  | ð |  | ð |  | ð |  | ð |  | ð |  | ð |  | ð |  | ï |  | ï |  | ï |  | ï |  | ï |  | ï |  | ï |  | ï |  | ï |  | ï |  | ï |  | ï
Start of Recharge Bus Bar Currents Can be reduced by also Moving Rectifiers
Rectifiers Moved to Balanced in Float
Frame |  | System |  |  | 1 |  | 2 |  | 3 |  | 4 |  | 5 |  | 6 |  | 7 |  | 8 |  | 9 |  | 10 |  | 11 |  | 12 |  | 13 |  | 14 |  | 15 |  | 16 |  | 17 |  | 18 |  | 19 |  | 20
Rectifiers |  | 72 |  |  | 3 |  | 4 |  | 3 |  | 4 |  | 3 |  | 4 |  | 3 |  | 4 |  | 4 |  | 4 |  | 4 |  | 4 |  | 4 |  | 4 |  | 4 |  | 3 |  | 4 |  | 2 |  | 4 |  | 3
Rectifier error |  | 0.48365 |  |  | -0.025818 |  | 0.46127 |  | -0.025818 |  | -0.28227 |  | -0.025818 |  | -0.28227 |  | -0.025818 |  | 0.46127 |  | 0.46127 |  | 0.46127 |  | 0.46127 |  | -1.0258 |  | 0.46127 |  | -1.0258 |  | 0.46127 |  | -0.025818 |  | 0.46127 |  | -0.63683 |  | -0.28227 |  | -0.025818
Battery Strings |  | 20 |  |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1 |  | 1
| slots to end |  |  |  | 64 | 60 |  | 56 |  | 52 |  | 48 |  | 44 |  | 40 |  | 36 |  | 32 |  | 28 |  | 24 |  | 20 |  | 16 |  | 12 |  | 8 |  | 4 |  | 8 |  | 12 |  | 16 |  | 20
| Rect error sum |  |  |  |  | -0.025818 |  | 0.43546 |  | 0.40964 |  | 0.12737 |  | 0.10155 |  | -0.18072 |  | -0.20654 |  | 0.25473 |  | 0.71601 |  | 1.1773 |  | 1.6386 |  | 0.61274 |  | 1.074 |  | 0.048193 |  | 0.50947 |  | 0.48365 |  | 0.94492 |  | 0.30809 |  | 0.025818
| Rects remaing |  |  |  |  | 69 |  | 65 |  | 62 |  | 58 |  | 55 |  | 51 |  | 48 |  | 44 |  | 40 |  | 36 |  | 32 |  | 28 |  | 24 |  | 20 |  | 16 |  | 13 |  | 9 |  | 7 |  | 3
| rect slot short to end |  |  |  |  | 9 |  | 9 |  | 10 |  | 10 |  | 11 |  | 11 |  | 12 |  | 12 |  | 12 |  | 12 |  | 12 |  | 12 |  | 12 |  | 12 |  | 12 |  | 5 |  | -3 |  | -9 |  | -17
Float Currents | Load | 11620 |  |  | 480 |  | 720 |  | 480 |  | 600 |  | 480 |  | 600 |  | 480 |  | 720 |  | 720 |  | 720 |  | 720 |  | 480 |  | 720 |  | 480 |  | 720 |  | 480 |  | 720 |  | 220 |  | 600 |  | 480
| Rectifier | 11620 |  |  | 484.1667 |  | 645.5556 |  | 484.1667 |  | 645.5556 |  | 484.1667 |  | 645.5556 |  | 484.1667 |  | 645.5556 |  | 645.5556 |  | 645.5556 |  | 645.5556 |  | 645.5556 |  | 645.5556 |  | 645.5556 |  | 645.5556 |  | 484.1667 |  | 645.5556 |  | 322.7778 |  | 645.5556 |  | 484.1667
| Bus Bars | 264.4444 | max |  |  | 4.1667 |  | -70.2778 |  | -66.1111 |  | -20.5556 |  | -16.3889 |  | 29.1667 |  | 33.3333 |  | -41.1111 |  | -115.5556 |  | -190 |  | -264.4444 |  | -98.8889 |  | -173.3333 |  | -7.7778 |  | -82.2222 |  | -78.0556 |  | -152.5 |  | -49.7222 |  | -4.1667
|  | 78.8304 | avg |  |  | ð |  | ï |  | ï |  | ï |  | ï |  | ð |  | ð |  | ï |  | ï |  | ï |  | ï |  | ï |  | ï |  | ï |  | ï |  | ï |  | ï |  | ï |  | ï
Start of Recharge | Load | 12782 |  |  | 528 |  | 792 |  | 528 |  | 660 |  | 528 |  | 660 |  | 528 |  | 792 |  | 792 |  | 792 |  | 792 |  | 528 |  | 792 |  | 528 |  | 792 |  | 528 |  | 792 |  | 242 |  | 660 |  | 528
| Rectifiers | 15840 |  |  | 660 |  | 880 |  | 660 |  | 880 |  | 660 |  | 880 |  | 660 |  | 880 |  | 880 |  | 880 |  | 880 |  | 880 |  | 880 |  | 880 |  | 880 |  | 660 |  | 880 |  | 440 |  | 880 |  | 660
| Batteries | 3058 |  |  | 152.9 |  | 152.9 |  | 152.9 |  | 152.9 |  | 152.9 |  | 152.9 |  | 152.9 |  | 152.9 |  | 152.9 |  | 152.9 |  | 152.9 |  | 152.9 |  | 152.9 |  | 152.9 |  | 152.9 |  | 152.9 |  | 152.9 |  | 152.9 |  | 152.9 |  | 152.9
| Bus Bars | 273.9 | max |  |  | -20.9 |  | -85.8 |  | -106.7 |  | -39.6 |  | -60.5 |  | 6.6 |  | -14.3 |  | -79.2 |  | -144.1 |  | -209 |  | -273.9 |  | -74.8 |  | -139.7 |  | 59.4 |  | -5.5 |  | -26.4 |  | -91.3 |  | -46.2 |  | 20.9
|  | 79.2 | avg |  |  | ï |  | ï |  | ï |  | ï |  | ï |  | ð |  | ï |  | ï |  | ï |  | ï |  | ï |  | ï |  | ï |  | ð |  | ï |  | ï |  | ï |  | ï |  | ð
Service and Assistance - +1 877 546 3243 | [6 empty] | PE.TechSupport@ge.com

## Instructions
Instructions Example system information is pre-entered - over-write it for your system. Enter your system information into the light green cells. Only Frames with Rectifier Positions, Battery Strings, or Load are considered present. To add a frame, add Rectifier Positions, Battery Strings, or Load to the frame. To remove a frame, delete its Rectifier Positions, Battery Strings, and Load. The "Original System" section show currents in the system. Other Sections show currents in the system after rectifiers and/or battery connections are moved to improve balance. If moving rectifiers or battery connections will reduce inter-frame bus bar currents, those currents are shown with red fill in the Original System section and with green fill in Other sections. If all rectifier positions are occupied, no rectifiers can be moved to improve balancing. Float current is most important because it is present most of the time. Discharge and Recharge are rare events of relatively short duration. Moving Rectifiers balances float current.
Battery Connections and Battery Strings per Frame Battery Connections input cell (light green) configures the balancer to split battery strings (or sections) by cabling a single string or section to multiple Frames. This allows you to input or the balancer to assign non-integer sets of strings to frames. For example, with Battery Connections set to 2, strings can be assigned to frames in increments of 0.5 (one of the 2 connections per string). A battery section is one or more strings connected in parallel, cabled and managed as a unit, by such system elements as contactors, battery disconnect switches, etc..
Notes
Rectifiers matched to load in float - G92
These notes are best viewed in Courier font with zoom to maintain fixed character spacing.
** indicates lines with functional names replacing cell references
parenthesis levels on following line
a b c d e f f e d c b gh i j j ih k kg lm n o o nm p pla
=MAX(MAX(MIN(ROUND(Rectifiers_InstalledSys * Load_Frame / Load_SysFloat + IF(FrameNumber <>1, SUM($E93:E93),0),0),G$18) ), (($D$19-IF(FrameNumber <>1, SUM($E$92:E$92),0))-SUM(I$18:$W$18))*(($D$19-IF(G$17 <>1, SUM($E$92:E$92),0)) >= SUM(I$18:$W$18)))
=MAX(
MAX(
MIN(ROUND(Rectifiers_InstalledSys * Load_Frame / Load_SysFloat + If(FrameNumber <>1, SUM($E93:E93) ,0),0),G$18)
** Min(Round(Rectifiers_InstalledSys * Load_Frame / Load_SysFloat + If(FrameNumber <>1, Sum(RectErrorFrame Prior Frames),0),0),RectifierPositions_Frame)
),
(($D$19 - IF(G$17 <>1, SUM($E$92:E$92) ,0)) - SUM(I$18:$W$18 ) ) * (($D$19 - IF(G$17 <>1, SUM($E$92:E$92) ,0)) >= SUM(I$18:$W$18) )
**((RectsSys - If(FrameNumer <>1, Sum(RectifierPositionsFrameAndPrior ,0)) - Sum(RectifierPositionsFollowingFrames) ) * ((Rectifiers_InstalledSys - If( <>1, Sum(RectifierPositionsFrameAndPrior) ,0)) >= SUM(RectifierPositionsFollowingFrames))
)
Battery Strings Balanced to Load - G72
=IF(Load_Frame>0,ROUND(BattCons*StringSys*Load_Frame/Load_SysFloat + IF(FrameNumber <>1, SUM(E73:$E73),0),0)/BattCons,0)
** SUM(E73:$E73),0),0) is the sum of battery string shortfall in prior frames (cumulative shortfall)
Rows and Columns not necessary for use of the calculator are hidden. To unhide Columns (Rows) Un-Protect the Worksheet - Tools ¦ Protection Select the right-most (top-most) visible column and the unlabeled area to its right (below) Right Click and select UnHide To Hide Columns (Rows) Select the first column to be Hidden Shift+Ctrl+Right-Arrow (Shift+Ctrl+Down-Arrow) to select all remaining Columns (Rows) to the end of the worksheet Protect the worksheet - Tools ¦ Protection ¦ Protect sheet