## Input Parameters
Power Express Reach Calculator |  | Version: | 2013-07-29
User entered data (Tab key toggles cursor between orange boxes)
Step 1 | What is the minimum input voltage at the source? |  | 57 | Volts
41.25 Volts is recommended for traditional systems
57 Volts is recommended for systems with converter boost in the limiter
Step 2 | What is the minimum input voltage required at the remote load? |  | 38 | Volts
Step 3 | How many Watts are needed at 48Volts in the remote device? |  | 86 | Watts
Step 4 | What wire gage do you use in your network for remote power?* |  | 12 | Gage
Results of Calculations
| The one way distance from the 96.6W power source to the remote cabinet is: |  | 1071 | Feet | VA Limit
Supporting Intermediate Results for each Option:
| Wire Conductivity | Ohms per thousand meters (1 conductor): | 5.61 | Ohms per thousand meters
VA Limit Calculations
|  | Max current at VA limit (96W): | 1.693 | Amps
|  | Round trip resistance at max current: | 3.6634 | Ohms
|  | Max Distance one way: | 1071 | Feet
|  | Voltage drop in wire | 6.2021 | Volts
|  | Voltage at remote end: | 50.7979 | Volts
|  | Headroom on Min Voltage (must be postive): | 12.7979 | Volts
Voltage Limit Calculations
|  | Current at Minimum Input Voltage at Remote Load: | 2.2632 | Amps
|  | Maximum Voltage Drop: | 19 | Volts
|  | Wire resistance of wire at voltage limit: | 8.3953 | Ohms
|  | Max Distance one way if V limited: | 2455 | Feet
|  | Number of Converter Cards Required: | #REF! | Cards
|  | Number of Pairs Required: | #REF! | Pairs

## Wire Resistance Data Set (hidden)
Size | Size | Dia | Cross Sectional Area |  | Weight | Copper | Resistance | Resistance
AWG | AWG | in | cir. mils | sq. in. | lb/1000ft | Resistivity | Ω/1000ft | Ω/1000m
Ω-ft
6.09e-08
-3 | 4/0 | 0.46 | 211600 | 0.16619 | 640.55 |  | 0.052768 | 0.17312
-2 | 3/0 | 0.40964 | 167806.4289 | 0.13179 | 507.9792 |  | 0.06654 | 0.21831
-1 | 2/0 | 0.3648 | 133076.5481 | 0.10452 | 402.8459 |  | 0.083905 | 0.27528
0 | 1/0 | 0.32486 | 105534.5006 | 0.082887 | 319.4713 |  | 0.1058 | 0.34712
1 | 1 | 0.2893 | 83692.6638 | 0.065732 | 253.3522 |  | 0.13341 | 0.43771
2 | 2 | 0.25763 | 66371.2998 | 0.052128 | 200.9175 |  | 0.16823 | 0.55194
3 | 3 | 0.22942 | 52634.8337 | 0.041339 | 159.3348 |  | 0.21214 | 0.69599
4 | 4 | 0.20431 | 41741.3208 | 0.032784 | 126.3582 |  | 0.2675 | 0.87762
6 | 6 | 0.16202 | 26251.3747 | 0.020618 | 79.4675 |  | 0.42534 | 1.3955
8 | 8 | 0.12849 | 16509.6518 | 0.012967 | 49.9776 |  | 0.67632 | 2.2189
10 | 10 | 0.1019 | 10383.0221 | 0.0081548 | 31.4312 |  | 1.0754 | 3.5282
12 | 12 | 0.080808 | 6529.9468 | 0.0051286 | 19.7673 |  | 1.7099 | 5.61
14 | 14 | 0.064084 | 4106.7239 | 0.0032254 | 12.4318 |  | 2.7189 | 8.9203
16 | 16 | 0.050821 | 2582.7441 | 0.0020285 | 7.8184 |  | 4.3232 | 14.1838
18 | 18 | 0.040303 | 1624.3037 | 0.0012757 | 4.917 |  | 6.8742 | 22.5532
19 | 19 | 0.035891 | 1288.1314 | 0.0010117 | 3.8994 |  | 8.6682 | 28.439
20 | 20 | 0.031961 | 1021.5346 | 0.00080231 | 3.0924 |  | 10.9304 | 35.861
21 | 21 | 0.028462 | 810.1138 | 0.00063626 | 2.4524 |  | 13.783 | 45.2198
22 | 22 | 0.025347 | 642.4494 | 0.00050458 | 1.9448 |  | 17.38 | 57.0212
23 | 23 | 0.022572 | 509.4856 | 0.00040015 | 1.5423 |  | 21.9158 | 71.9023
24 | 24 | 0.020101 | 404.0404 | 0.00031733 | 1.2231 |  | 27.6354 | 90.6672
25 | 25 | 0.0179 | 320.4186 | 0.00025166 | 0.96996 |  | 34.8475 | 114.3292
26 | 26 | 0.015941 | 254.1035 | 0.00019957 | 0.76922 |  | 43.9419 | 144.1665